## Slide 1: Performance-based approach for complex structure design
Samuele Sassi, FSC Engineering Srl, Fire Engineering and Fire Safety
Design Consultants, Milan
HRVATSKA KOMORA INŽENJERA GRAĐEVINARSTVA
Dani Hrvatske komore inženjera građevinarstva Opatija, 2019.
Ing. Samuele Sassi
Notes: 1

## Slide 2
Identification of
performance levels
performance levels
(I, II, III, IV, V)
Compliant solution
Alternative solution
(FSE)
Fire resistance
- Prescriptive standard
- fire load (EN 1991-2)
verification according to natural fire curves
verification according to Standard fire curves
Choice of
type of solution

## Slide 3: PERFORMANCE LEVELS

## Slide 4
STRUCTURAL FIRE RESISTACE ANALYSIS
Prescriptive approach
(standard or fire load )
Performance based approach
Nominal Curves
Natural Curves
Test based curves
Simplified models
Advanced models
Parametric curves
Local fire model
Single zone model
Two zone model
CFD models
Ref.
EN 1991-1-2
Italian law and regulamentations
Nominal standard (ISO 834)
Hydrocarbons fire
External fire
Notes: 45’’

## Slide 5
BRESCIA SKYLINE 18

## Slide 13
Local fire
Local fire + natural fire curves

## Slide 14
Efi,d < Rfi,d,t

## Slide 15
mt=o
mt=o
mt=o
mt=o
mt=o
mt=o
Fv1(t=o)
Fv2(t=o)
Fo1(t=o)
Fo2(t=o)
F’v1(t=o)
F’v2(t=o)
F’o1(t=o)
F’o2(t=o)
ANALISI PER SINGOLI ELEMENTI
O PER SOTTOSTRUTTURE

## Slide 16
Define the WORST FIRE SCENARIO
(position, fire curve, etc.)
Check the behaviour of the structure under fire conditions
SFSE (Structural Fire Safety Engineering)
Define the targets
(reduce costs of maintenance, beauty of the building, ensure the stability of
the building, etc.);
Focalize the main activities inside the building;
Understand the global behaviour of the structure
(it is important define the structural hierarchy of the elements - robustness);

## Slide 17
2 zone
1 zone
Natural Fire curve
flashover
Tup > 500°C
hup > 80% h
ZONE MODEL

## Slide 18
Torre Intesa San Paolo (Torino) - Greenhouse

## Slide 19
Cases studies: Piedmont Region Headquarters - Turin

## Slide 20
Cases studies: Piedmont Region Headquarters - Turin

## Slide 21
Design Fire Scenarios
• Fire:
1 – Fire at leve 0 Grand Space
2 – Fire at level -2 Grand Space
3&4 – Fire iside the office level
5&6 – Fire inside the Satellite
Cases studies: Piedmont Region Headquarters - Turin

## Slide 22
Fire Scenario 1 – Fire inside the Grand Space at level 0
Cases studies: Piedmont Region Headquarters - Turin

## Slide 23: BOUNDARIES scenario 1
• Fire • The fire development coefficient is 0.047 kW/s2.
• The are no sprinklers and the fire reached maximum effect of 5 MW after 326 s. The fire load is assumed to be constant of 10 minutes after its reached maximum. After this it decreases linearly.
• Ventilation • Smoke beam detectors are activated after 30 s and opens the openings in the bottom at level -2 for fresh air and the openings in the top.
Cases studies: Piedmont Region Headquarters - Turin

## Slide 24
Fire Scenario 1 – Fire inside the Grand Space at level 0
Cases studies: Piedmont Region Headquarters - Turin

## Slide 25
Fire Scenario 1 – Fire inside the Grand Space at level 0
Cases studies: Piedmont Region Headquarters - Turin

## Slide 26
Fire Scenario 2 – Fire inside the Grand Space at level -2
Cases studies: Piedmont Region Headquarters - Turin

## Slide 27: BOUNDARIES scenario 2
• Fire • The fire development coefficient is 0.047 kW/s2.
• The are no sprinklers and the fire reached maximum effect of 5 MW after 326 s. The fire load is assumed to be constant of 10 minutes after its reached maximum. After this it decreases linearly.
• Ventilation • Smoke beam detectors are activated after 30 s and opens the openings in the bottom at level -2 for fresh air and the openings in the top.
Cases studies: Piedmont Region Headquarters - Turin

## Slide 28
Fire Scenario 2 – Fire inside the Grand Space at level -2
Cases studies: Piedmont Region Headquarters - Turin

## Slide 29
Fire Scenario 2 – Fire inside the Grand Space at level -2
Cases studies: Piedmont Region Headquarters - Turin

## Slide 30
Fire Scenario 3 & 4 – Fire inside the office
Cases studies: Piedmont Region Headquarters - Turin

## Slide 31: BOUNDARIES Scenario 3 – Fire inside the office no sprinkler
Fire
The fire development coefficient is 0.047 kW/s2.
Fire develops to up to an HRR value of 6 MW. It reaches its maximum effect after 326 s and remains constant for 1 hour. .
Ventilation
Smoke detectors are activated after 40 s and gives start signal for the ventilation. The ventilation has full capacity after 100 s. A ramp up time of 60 s is assumed.
The extracted air in the office is 12.000 m3/h
Air is supplied by two openings. Each opening has a area of 0.5 m x 0.5 m
Cases studies: Piedmont Region Headquarters - Turin

## Slide 32: BOUNDARIES Scenario 4– Fire inside the office with sprinkler
• Fire • The fire development coefficient is 0.047 kW/s2. • The sprinklers are activated after 145 s and the fire load is thereby reduced to 0.98 MW.
• Ventilation • Smoke detectors are activated after 40 s and gives start signal for the ventilation. The ventilation has full capacity after 100 s. A ramp up time of 60 s is assumed. • The extracted air in the office is 12.000 m3/h • Air is supplied by two openings. Each opening has a area of 0.5 m x 0.5 m
Cases studies: Piedmont Region Headquarters - Turin

## Slide 33
Fire Scenario 3 & 4 – Fire inside the office
Cases studies: Piedmont Region Headquarters - Turin

## Slide 34
Fire Scenario 3 & 4 – Fire inside the office
Cases studies: Piedmont Region Headquarters - Turin

## Slide 35
Fire Scenario 3 & 4 – TEST FOR FAÇADE EW 60 (i->o)
Cases studies: Piedmont Region Headquarters - Turin

## Slide 36
Fire Scenario 5 & 6 – Fire inside the Satellite
Cases studies: Piedmont Region Headquarters - Turin

## Slide 37: BOUNDARIES Scenario 5 – Fire inside the satellite no water-mist
• Fire • The fire development coefficient is 0.047 kW/s2. •HRR load reaches 5 MW and remains constant for 15 minutes
Cases studies: Piedmont Region Headquarters - Turin

## Slide 38: BOUNDARIES Scenario 6 – Fire inside the satellite with water-mist
• Fire • The fire development coefficient is 0.047 kW/s2. •The water mist are activated after 46 s and the fire load is thereby reduced to 0.1 MW.
Cases studies: Piedmont Region Headquarters - Turin

## Slide 39
Fire Scenario 5 – Fire inside Satellite – no water mist
Cases studies: Piedmont Region Headquarters - Turin

## Slide 40
EW 60 io
EI 60 bidirezionale
EI 120
after Fire Brigades exception
EI 60
Prescriptive solution VS FSE solution
• NO Reaction of fire resistant glass in some weather condition
• NO maintenance of fire resistant glass
• NO maintenance of intumescent painting
• NO stuctural problem for the weight of water curtain
• SAVE SOME MILLIONS OF EUROS
Cases studies: Piedmont Region Headquarters - Turin

## Slide 41
"Glasshouse":
Steel-frame structure
Tower’s main body :
- Composite Steel/R.C.
- Steel
- Reinforced Concrete
Transfer nord and sud
Composite Steel/R.C.
Basaments:
Reinforced Concrete
Cases studies: Torre Intesa San Paolo - Turin

## Slide 42
Cases studies: Torre Intesa San Paolo - Turin

## Slide 43
"Transfer" structures’ elements, Nord and Sud
Cases studies: Torre Intesa San Paolo - Turin

## Slide 44
DESIGN CRITERIA (Targets)
Failure of one megacolumn on 8th and 9th floor on axes 10-13-16;
Absence of truss elements on axis 13;
Concrete core’s resistance contribution lack on torsion;
No resistance contribution by bracings on axis 10;
Failure of a strand in one of East-West façades (axes B and J);
IMMEDIATE USE OF THE TOWER AFTER AN EVENTUAL FIRE (NO GLOBAL DAMEGES ON THE STRUCTURE)
Cases studies: Torre Intesa San Paolo - Turin

## Slide 45
1st fire scenario is performed with 2 hours of ISO 834 standard fire exposure along 8 m piece of a Megacolumn (MC), corresponds to a local fire at the tip or base of MC, between L0 and L7;
2nd fire scenario is performed with 2 hours of ISO 834 standard fire exposure for the entire height of MC between L0 and L7 (L=32.5 m);
Cases studies: Torre Intesa San Paolo - Turin
FIRE SCENARIOS
3rd scenario is performed with ISO 834 standard fire curve in two office levels (from level 8 to the top), which puts at risk the stability of the bracings on B, J and 10 axes (repeated for the entire height of the tower).

## Slide 46
MEGACOLUMNS
PROGETTO COSTRUTTIVO:
STRUTTURA MISTA ACCIAIO / C.A.
Cases studies: Torre Intesa San Paolo - Turin

## Slide 47
Cases studies: Te Intesa San Paolo - Turin

## Slide 48
DESIGN CRITERIA (Targets)
Failure of one megacolumn on 8th and 9th floor on axes 10-13-16;
Absence of truss elements on axis 13;
Concrete core’s resistance contribution lack on torsion;
No resistance contribution by bracings on axis 10;
Failure of a strand in one of East-West façades (axes B and J);
IMMEDIATE USE OF THE TOWER AFTER AN EVENTUAL FIRE (NO GLOBAL DAMEGES ON THE STRUCTURE)
Cases studies: Torre Intesa San Paolo - Turin

## Slide 49
LA TORRE:
MECAGOLONNE
1st fire scenario is performed with 2 hours of ISO 834 standard fire exposure along 8 m piece of a Megacolumn (MC), corresponds to a local fire at the tip or base of MC, between L0 and L7;
2nd fire scenario is performed with 2 hours of ISO 834 standard fire exposure for the entire height of MC between L0 and L7 (L=32.5 m);
Cases studies: Torre Intesa San Paolo - Turin

## Slide 50
LA TORRE:
Transfer sud
1st fire scenario is performed with 2 hours of ISO 834 standard fire exposure along 8 m piece of a Megacolumn (MC), corresponds to a local fire at the tip or base of MC, between L0 and L7;
2nd fire scenario is performed with 2 hours of ISO 834 standard fire exposure for the entire height of MC between L0 and L7 (L=32.5 m);
Cases studies: Torre Intesa San Paolo - Turin

## Slide 51
3rd scenario is performed with ISO 834 standard fire curve in two office levels (from level 8 to the top), which puts at risk the stability of the bracings on B, J and 10 axes (repeated for the entire height of the tower).
Cases studies: Torre Intesa San Paolo - Turin

## Slide 52: PALAZZO ITALIA

## Slide 53
PALAZZO ITALIA

## Slide 54
PALAZZO ITALIA – Scenario 1

## Slide 55
PALAZZO ITALIA – Scenario 2

## Slide 56
PALAZZO ITALIA – Scenario 3

## Slide 57
PALAZZO ITALIA – Risultati scenario 1

## Slide 58
PALAZZO ITALIA – Risultati scenario 2

## Slide 59
PALAZZO ITALIA – Risultati scenario 3

## Slide 60
MALL OF QATAR - DOHA

## Slide 61
MALL OF QATAR - DOHA

## Slide 62
INCENDIO REALE IN COPERTURA
MALL OF QATAR - DOHA

## Slide 63
INCENDIO REALE IN COPERTURA
MALL OF QATAR - DOHA

## Slide 64
INCENDIO REALE IN COPERTURA
MALL OF QATAR - DOHA

## Slide 65
INCENDIO REALE IN COPERTURA
MALL OF QATAR - DOHA

## Slide 66
INCENDIO REALE IN COPERTURA
MALL OF QATAR - DOHA

## Slide 67
INCENDIO REALE IN COPERTURA
MALL OF QATAR - DOHA